## Slide 1
DIGITAL TWIN · DATA-CENTER COOLING CONTROL
Digital Twin Dual-Loop Control Framework
Weekly setpoint optimization with EnergyPlus 9.5 simulated in the loop — no surrogate, no MPC
INNER LOOP · planning, fast, all inside the twin (no human)
Forecaster week-ahead IT load + weather
›
Beam Search best-first over 3 setpoints
›
EnergyPlus 9.5 full-week twin scores each
›
Safety Filter reject inlet > 26 °C
›
Recommendation best feasible plan.json
OUTER LOOP · weekly operation, human-in-the-loop
Pre-validation independent replay + report
›
Expert Approve / Reject robust-feasibility gate
›
Deploy → Realized KPIs sim plant; safety backstop
›
Calibrate + Re-plan realized data tunes next week ↺
11.4% HVAC energy ↓
0 violations inlet ≤ 26 °C every step (acceptance week)
3 global setpoints → 45 actuators CRAH supply-air temp · CRAH airflow · CHWST
GDS tropical data center · dctwin / BCVTB / Docker · FastAPI + React operator app with 3-D digital-twin view

## Slide 2
HIGH-FIDELITY, SAFE WEEKLY RECOMMENDATIONS
Closing the Fidelity & Safety Gap
⚠
The gap we found: a twin-“feasible” plan (0 violations) ran 666 of 672 steps over the 26 °C cap — 13× energy — once the real plant differed from the twin.
① SAFETY GATE · shipped & merged
›
Robust-feasibility deploy gate blocks any unsafe plan
›
Deploy-time backstop on a realized inlet breach (still learns)
›
Calibration de-poison: σ-floor + raw-residual fit
›
Pre-validation = real independent replay + report
›
Web-app hardening: status-gated edits, fail-closed auth
② VISIBILITY & HARDENING · shipped
›
Per-step inlet trajectory: nominal vs worst-case, pre-approval
›
History predicted-vs-realized energy trend
›
Startup fail-fast: bad plan rejected before E+ runs
›
Real-weather forecast + honest labels & uncertainty bands
›
Robust scenario error-handling + container teardown
212 backend tests
59 frontend tests
Docker EnergyPlus integration
spec → plan → TDD multi-agent reviewed
Next real plant telemetry / BMS adapter · per-hall & time-block setpoints · ML forecaster · multi-week loop convergence